| APPROVALS | DATE | REV | DCN NO. | BY | CHECK | DCC | DATE |
| --- | --- | --- | --- | --- | --- | --- | --- |
| AUTHOR: | 3/2/11 | V1 | For Installation |  |  |  |  |
| CHECKED: |  |  |  |  |  |  |  |
| APPROVED: |  |  |  |  |  |  |  |
| DCC RELEASE |  |  |  |  |  |  |  |

TABLE OF CONTENTS

1.0	SCOPE

2.0	CODES AND STANDARDS

3.0	MATERIAL/MANUFACTURING REQUIREMENTS

4.0	EXAMINATION AND TESTING

5.0	LINE NUMBER SYSTEM

6.0	VALVE AND INSTRUMENT NUMBERING SYSTEM

7.0	PIPING DESIGN AND MATERIAL SPECIFICATIONS

pIPE cLASSES

1B1	150# CLASS STAINLESS STEEL 304 - CRYOGENIC

1B2	150# CLASS STAINLESS STEEL 304 - NON-CRYOGENIC

C2	TYPE "L" COPPER TUBING - GENERAL NON-CRYOGENIC

T1	316 STAINLESS STEEL TUBING - CRYOGENIC

T2	304 STAINLESS STEEL TUBING - GENERAL NON-CRYOGENIC

T3	304L STAINLESS STEEL TUBING - VACUUM

T4	304L STAINLESS STEEL TUBING - ULTRA HIGH VACUUM

T5	304L STAINLESS STEEL TUBING - CLASS 5 CLEAN AIR

C1               	TYPE “L” COPPER TUBING - CRYOGENIC

# 1.0	SCOPE

# The following piping and material specifications define the piping and fittings to be used for 	the LIGO Vacuum Equipment.

# 2.0	CODES AND STANDARDS

## 2.1	Priority of Codes and Standards are as follows:

1.	Codes (highest priority)

## 2.	This specification

## 2.2	Applicable Codes and Standards (Latest Edition)

ANSI -	American National Standards Institute

B31.3	Chemical Plant and Petroleum Refinery Piping (for process 			piping only)

B31.5	Refrigeration Piping
	B36.19	Stainless Steel Pipe
	B16.5	Pipe Flanges and Flange Fittings

ASTM -	American Society of Testing and Materials

A380-88		Standard Practice for Cleaning and De-scaling Stainless Steel

E427-71(81)		Standard Practice for Testing for Leaks Using the Halogen Leak Detector

E493-73(80)		Standard Practice for Testing for Leaks Using the Mass Spectrometer Leak 				Detector in the Inside-Out Testing Mode

E498-73(80)		Standard Test Method for Leaks Using the Mass Spectrometer Leak 					Detector or Residual Gas Analyzer in the Tracer Probe Mode

E499-73(80)		Standard Methods of Testing for Leaks Using the Mass Spectrometer Leak 				Detector Probe Mode

## 2.3	Specification Compliance

## The equipment shall comply with any drawings, data sheets, specifications, codes and standards (latest editions) referred to or attached as part of this specification.  State or local codes or regulations, if applicable, will be provided as an attachment to this specification.  The vendor is responsible for compliance with such standards, specifications, codes and regulations, if attached.

# 3.0	MATERIAL/MANUFACTURING REQUIREMENTS

All materials used to manufacture the piping, tubing, flanges or fittings, as designated per this specification, are to be of U.S.A. origin and manufacture.

# 4.0	EXAMINATION AND TESTING

Examination and Pressure Testing as required by ANSI B31.3

# 5.0	line number system

## 4.1	Lines shall be numbered according to the following chart:

2	PL	008	XYZ	3	HC	FP3

Insulation Mat’l
	(See Section 5.5)
	Service

Insulation Code

(See Section 5.4)

Insulation Thickness

Piping Specification
	Designation (See Section 5.3)

Sequential Number

Fluid Service Code (See Section 5.2)

Line Size (Nominal Pipe, Inches).  (Copper Tube Designated By Nominal Size, Not Od)

## 5.2	Fluid Codes

Code		Fluid

IA			Instrument Air

CA			Class 100 Clean Air

CWS			Cooling Water Supply

CWR			Cooling Water Return

NGS			Natural Gas Supply

LN2			Liquid Nitrogen

GN2			Gaseous Nitrogen

PV			Process Vacuum

PUV		Process Ultra High Vacuum

VA			Vent and Relief to ATM

N2			Nitrogen Gas

N			Nitrogen (Either Gas or Liquid)

## 5.3	Piping Specification Designation

"X" First Digit Identifiers

1 = 150 #  ANSI

"Y" Second Digit Identifiers

A = 6061 T6 Aluminum
B = 304 Stainless Steel
C = Type L Copper Tubing

T =  Stainless Steel Tubing

"Z" Third Digit Identifiers
1 = Cryogenic

2 = Non-Cryogenic

3 = Vacuum

= Ultra High Vacuum

= Class 100 Clean Air

## 5.4	Insulation Service

Insulation

Symbol  			Insulation Service

HC				Hot and Cold

C				Cold Conservation

PC				Personnel Protection Cold

PH				Personnel Protection Hot

VJ				Vacuum Jacketed

## 5.5	Insulation Material Codes

### FP3	1" Fiberglass Inner	2" Polyisocyanurate Outer

### FP3.5	1" Fiberglass Inner	2 1/2" Polyisocyanurate Outer

### FP4	1" Fiberglass Inner	3" Polyisocyanurate Outer

### If no insulation material code appears in the line number then it shall be understood that no insulation is required.

# 6.0	valve and instrument number system

Control valves, manual valves and associated instruments shall be designated according to P&ID Drawing Symbols.  If the required designation is not specified on the drawing, then ISA-S5.1,       Table 1 will take precedence.

PV   -   A	BB

Sequential (Loop) Number

Station Identification

Functional Identification

# Manual valves that do not carry an instrument loop numbers (described above) shall be assigned one of the following valve type descriptions, preceded by the valve size in inches.

| Type | Description |
| --- | --- |
| GVHV | Gate Valve, High Vacuum, SS, Viton Seals, Handwheel or Lever, CF Conn. |
| GVUH | Gate Valve, Ultra High Vacuum, SS, Viton Seals, Handwheel, CF Conn. |
| AVHV | Angle Valve, High Vacuum, SS, Viton Seals, Handwheel, ISOKF or K Conn. |
| AVUV | Angle Valve, Ultra High Vacuum, SS, Metal Seals, Handwheel, CF Conn. |
| IRV | Instrument Root Valve, SS |
| VJV | Vacuum Jacketed Valve, SS |
| BVCR | Ball Valve, Cryogenic, SS, 3 Piece |
| BVCA | Ball Valve, Class 100 Clean Air, SS, 3 Piece |
| GLV | Globe Valve |
| BVU | Ball Valve, Utility, Brass or Bronze |
| VSOV | Vacuum Seal-Off Valve, SS |
| VSOO | Vacuum Seal-Off Valve Operator, SS |

1B1

PIPING DESIGN AND MATERIAL SPECIFICATION

Service:				Cryogenic

Primary Rating:			150# ANSI 304 SSTL

Design Conditions:

Pressure			0 To 192 PSIG

Temperature			-320(F To 350(F

Corrosion Allowance		Zero

Pipe:

12" and smaller		ASTM A312 TP304

Pipe Schedule:

1 1/2” and smaller	Schedule 10S SMLS

8" and smaller			Schedule 10S SMLS or EFW

10" thru 12"			Schedule 10S EFW

Note:	Vacuum jacketed piping will be designed and fabricated in accordance with the manufacturer’s standard, and  Spec. V049-2-016.

Fittings:

1 1/2” and smaller		Socket Welded 3000#

2" and larger		Butt Weld

ASTM A403 WP304 WPS, WPW

O'Let’s ASTM A182-F304

Flanges:	Not allowed, except on atmospheric vent lines as indicated on PSID’s.  Flanges on the vent line, (which mate to a flat faced flange on the vacuum equipment) shall be stainless steel raised-face design. Flanged joints shall have spiral wound, stainless steel gaskets, Flexitallic or equal.

Valves:	Valves shall be furnished under their own unique specification.

1B1 Cont. on next page

1B1

Branch Connections:

Run

Size "

½	04							04 - Tee

¾	06	04						05 - Sockolet

1	12	06	04					06 - Tee Then

1½	05	05	06	04				Reducer or

2	05	05	06	06	04			Reducing Tee

3	05	05	05	05	06	04		12 - Bw O'let

4	05	05	05	05	12	06	04

6	05	05	05	05	12	12	06	04

8	05	05	05	05	12	12	12	06	04

10	05	05	05	05	12	12	12	12	06	04

12	05	05	05	05	12	12	12	12	12	06	04

Branch Size	½	¾	1	1½	2	3	4	6	8	10	   12

1B2

PIPING DESIGN AND MATERIAL SPECIFICATION

Service:			Non-Cryogenic – Clean

Primary Rating:			150# ANSI 304 SSTL

Design Conditions:

Pressure			0 to 192 PSIG

Temperature			-20>(F to 350(F

Corrosion Allowance		Zero

Pipe:

12" and smaller		ASTM A312 TP304

Pipe Schedule:

1 1/2” and smaller	Schedule 10S SMLS

8" and smaller			Schedule 10S SMLS or EFW

10" thru 12"			Schedule 10S EFW

Fittings:

1 1/2” and smaller		Socket Welded 3000#

2" and larger			Butt Weld

ASTM A403 WP304 WPSs, WPW

Elbow O'Let ASTM A182-F304

Flanges:	2” and larger ANSI 150# RF, ASTM A182 F304, Weldneck with o-ring gaskets.

Gaskets:	O-ring, Viton non-lubricated, cleaned and sealed for shipment.

Valves:	Valves shall be furnished under their own unique specification.

1B2  Cont. on next page.

1B2

Branch Connections:

Run

Size "

½	04							04 - Tee

¾	06	04						05 - Sockolet

1	12	06	04					06 - Tee Then

1½	05	05	06	04				Reducer Or

2	05	05	06	06	04			Reducing Tee

3	05	05	05	05	06	04		12 - BW O'let

4	05	05	05	05	12	06	04

6	05	05	05	05	12	12	06	04

8	05	05	05	05	12	12	12	06	04

10	05	05	05	05	12	12	12	12	06	04

12	05	05	05	05	12	12	12	12	12	06	04

Branch Size	½	¾	1	1½	2	3	4	6	8	10	   12

Notes:

1.	Piping and fittings to be internally cleaned, dried and ends sealed during shipping, storing and installation.

2.	ID of pipe and fittings to be free of hydrocarbon contamination, or dirt. of any kind.

3.	Surface finish to be standard white pickled ID and O.D.

4.	Tube bending - the following is not allowed:  Sand packing, Mechanical scratches on tube I.D., Any type of lubricant.

5.	Material manufactures certificate of compliance to applicable ASTM specifications are required and must accompany shipment.

6.	Tubing, flanges and fittings to be etched or stamped with manufacturers name, part number and material type.

C2

PIPING DESIGN AND MATERIAL SPECIFICATION

Service:			Gaseous Nitrogen, Cooling Water, Instrument Air

Design Conditions:

Pressure		200 PSIG

Temperature		-20(F To 150(F

Corrosion Allowance	Zero

Tube:	All Sizes	Type "L" Copper - Hard Drawn ASTM B88, B280, Copper Tube Designated By Its Nominal Sizes, Not OD on P&ID’s and Piping Drawings.

Note:	Copper tube and fittings are to be specified on Buyer’s BOM by the actual O.D. of the tube.

Fittings:	All sizes	Wrought Copper ASTM B75

All Fittings to be female solder cup ends.

Brass Parker CPI tube fittings (or equal).

Unions:	1/4” to 1” 	Brass Parker CPI tube fittings (or equal) may also be used.

Valves:		Valves  shall be furnished under their own unique specification.

Soldering:	All joints in wrought copper fittings shall be soldered using 95-5 Tin-Antimony.

Notes:

1.	Tubing is to be internally cleaned and the ends sealed during shipping, storing and installation.  Spools are to have all flux residue, grit, splatters or dirt removed before installation.

2.	Fittings are to be cleaned after manufacturing and sealed in plastic during shipping, storing and installation.

T1

PIPING DESIGN AND MATERIAL SPECIFICATION

Service:				Cryogenic

Design Conditions:

Pressure		0 to 300 PSIG

Temperature		-320(F to 350(F

Corrosion Allowance	Zero

Tube:

All Sizes		ASTM A269 GR 304L SMLS

Tube sizes designated by OD dimensions.

Tube Size (Od):	Minimum Wall Thickness (Inches)

1/4"			0.035"

3/8"			0.035"

1/2"			0.049"

3/4"			0.049"

1"			0.065"

Fittings:	All Fittings to be Parker Weld tube fittings SA479 Or ASTM A276 GR TP316 and ASTM A182 GR TP316, or equal.

Valves:	Valves shall be furnished under their own unique specification.

Notes:

1.	Tubing to be internally cleaned, dried and ends sealed during shipping, storing and installation.  Tube ID to be free of hydrocarbon contamination.

2.	Fittings to be cleaned after manufacturing and sealed in plastic bags during shipping, storing and installation.

3.	Tubing surface finish to be standard white pickled I.D. & O.D.

T2

PIPING DESIGN AND MATERIAL SPECIFICATION

Service:				Non-Cryogenic

Design Conditions:

Pressure		0 to 300 PSIG

Temperature		-20(F To 350(F

Corrosion Allowance	Zero

Tube:

All Sizes		ASTM A269 GR TP304 SMLS

Tube sizes designated by OD dimensions.

Tube Size (Od):	Minimum Wall Thickness (Inches)

1/4"			0.035"

3/8"			0.035"

1/2"			0.049"

3/4"			0.049"

1"			0.065"

Fittings:	All fittings to be Parker A-LOK tube fittings SA479 or ASTM A276 GR TP316 and ASTM A182 GR TP316 or equal.

Valves:	Valves shall be furnished under their own unique specification.

Note:

1.	Tubing to be internally cleaned, dried and ends sealed during shipping, storing and installation.  Tube ID to be free of hydrocarbon contamination.

2.	Fittings to be cleaned after manufacturing and sealed in plastic bags during shipping, storing and installation.

3.	Tubing surface finish to be standard white pickled I.D. & O.D.

T3

PIPING DESIGN AND MATERIAL SPECIFICATION

Service:				Process Vacuum

Design Conditions:

Pressure			Vacuum 10-5 Torr to 2 PSIG

Temperature		-20(F to 150(F

Corrosion Allowance	Zero

Tube: (Tube Sizes Designated By OD Dimensions)

All sizes up to 1”		ASTM A269 GR TP304L SMLS

1 1/2” and larger		ASTM A269 GR TP304L SMLS or welded.

Tube		Minimum Wall 	Conflat						Thru

Size		Thickness	Flange			No.	B.C.		Hole

(OD):		(Inches)		Size			Bolts	Dia.		Dia.

1/4"		0.035"		1 1/3” Nom. O.D.		6	1.062”		.172”

3/8"		0.035"		1 1/3” Nom. O.D.		6	1.062”		.172”

1/2"		0.035"		1 1/3” Nom. O.D	.	6	1.062”		.172”

3/4"		0.035"		2 1/8” Nom. O.D.		4	1.625”		.265”

1"1		0.065"		2 3/4” Nom. O.D.		6	2.312”		.265”

1 1/2"		0.065"		2 3/4” Nom. O.D.		6	2.312”		.265”

2”		0.065"		3 3/8” Nom. O.D.		8	2.85”		.332”

2 1/2”		0.065”		4 1/2” Nom. O.D.		8	3.628”		.332”

4”		0.083”		6” Nom. O.D.		16	5.128”		.332”

6"		0.083		 8” Nom. O.D.		20	7.128”		.332”

8”		0.120		10”Nom.O.D.		24	9.128”		.332”

10”		0.120		12”Nom. O.D.		32	11.181”		.332”

12”		0.120		14”Nom.O.d.		30	12.810”		.390”

14”		0.120		16 1/2”Nom.O.D.		36	15.310”		.390”

Flanges:	All flanges to be Conflat, ISO Large Flange or KF tube fittings 304L Stainless Steel.

Flange bolts and washers to be stainless steel with silicon bronze nuts.

T3  Cont. on next page.

T3

Fittings:	All fittings to be 304L butt weld or flanged O.D. tube, wall thickness to match tube wall thickness listed above.

Valves:	Valves shall be furnished under their own unique specification.

Notes:

1.	Tubing to be internally cleaned, dried and ends sealed during shipping, storing and installation.  Tube ID to be free of hydrocarbon contamination.

2.	Fittings to be cleaned after manufacturing and sealed in plastic bags during shipping, storing and installation.

- Tubing surface finish to be standard white pickled I.D. & O.D. bright-annealed finish is allowed as an alternate.

4.	Tube bending - The following is not allowed:  Sand packing, mechanical scratches on tube I.D., or any type of lubricant.

5.	Material manufactures certificate of compliance to applicable ASTM specifications are required and must accompany shipment.

6.	Tubing, flanges and fittings to be etched or stamped with manufacturers name, part number and material type.

7.	Conflat flanges to be made from either electro slag remelt, vacuum remelt or cross forged material.

8.	Gaskets for ISO flanges to be 304S/S with baked Viton o-rings.

T4

PIPING DESIGN AND MATERIAL SPECIFICATION

Service:				Process Ultra High Vacuum

Design Conditions:

Pressure			Vacuum 10-10 Torr to 2 PSIG

Temperature		-20(F to 150(F

Corrosion Allowance	Zero

Tube:	(Tube sizes designated by OD dimensions)

All sizes up to 1”		ASTM A269 GR TP304L SMLS

1 1/2” and larger		ASTM A269 GR TP304L SMLS or welded.

Tube		Minimum Wall 	Conflat						Thru

### Size		Thickness	Flange			No.	B.C.		Hole

(Od):		(Inches)		Size			Bolts	Dia.		Dia.

1/4"		0.035"		1 1/3” Nom. O.D.		6	1.062”		.172”

3/8"		0.035"		1 1/3” Nom. O.D.		6	1.062”		.172”

1/2"		0.035"		1 1/3” Nom.. O.D.	6	1.062”		.172

3/4"		0.035"		2 1/8” Nom.. O.D.	4	1.625”		.265”

1"		0.065"		2 3/4” Nom. O.D.		6	2.312”		.265”

1 1/2"		0.065"		2 3/4” Nom.. O.D.	6	2.312”		.265”

2”		0.065"		3 3/8” Nom. O.D.		8	2.85”		.332”

2 1/2”		0.065”		4 1/2” Nom.. O.D.	8	3.628”		.332”

4”		0.083”		6” Nom.  O.D.		16	5.128”		.332”

6"		0.083		8” Nom.  O.D.		20	7.128”		.332”

8”		0.120		10”Nom. O.D.		24	9.128”		.332”

10”		0.120		12”Nom. O.D.		32	11.181”		.332”

12”		0.120		14”Nom. O.D.		30	12.810”		.390”

14”		0.120		16 1/2”Nom. O.D.	36	15.310”		.390”

T4  Cont. on next page

T4

Flanges:	All flanges to be Conflat, 304L Stainless Steel.  Flanges with 1/2 nipples to have a minimum wall thickness per table (page 16), also see note 7.

Bolts and washers to be stainless steel with silicon bronze nuts and washers.

Fittings:	All fittings to be 304L butt weld or flanged O.D. tube.  Wall thickness to match tube wall thickness listed in table (page 16).

Valves:	Valves shall be furnished under their own unique specification.  Valves whose seats form part of the UHV boundary shall be all metal.

Cleaning:	Surfaces exposed to vacuum shall be cleaned and protected by a Buyer approved procedure suitable for UHV service.

Notes:

1.	Tubing to be internally cleaned, dried and ends sealed during shipping, storing and installation.  Tube ID to be free of hydrocarbon contamination.

2.	Fittings and conflat - 1/2 nipples to be cleaned after manufacturing and sealed in plastic bags during shipping, storing and installation.

3.	Tubing surface finish to be standard white pickled I.D. & O.D.

4.	Material manufacturers Certificate of Compliance to applicable ASTM specifications are required and must accompany shipment.

5.	Tubing, flanges and fittings to be etched or stamped with manufacturers name, part number, material type and customers PO number on the outside surface.

6.	Conflats shall be made from 304L material suitable for ultra high vacuum service.

7.	All welding exposed to vacuum shall be done by the tungsten-arc inert-gas (TIG) process.  Exceptions may be allowed subject to approval by the Buyer.  Welding techniques shall be made in accordance with the best ultra high vacuum practice to eliminate any virtual leaks in the welds; i.e., All vacuum welds shall be, wherever possible, internal and continuous; all external welds added to these for structural purposes shall be intermittent to eliminate trapped volumes.  Defective welds shall be repaired by removal to sound metal and rewelding.  All vacuum weld procedures shall include steps to avoid contamination of the heat affected zone with air, hydrogen, or water.  This requires that inert purge gas, such as argon, be used to flood the vacuum side of heated portions.  Vendors to provide weld procedures, with weld cleaning procedures for approval by the Buyer.

T5

PIPING DESIGN AND MATERIAL SPECIFICATION

Service:				Class 100 Clean Air

Design Conditions:

Pressure			Vacuum to 2 PSIG

Temperature		-20(F to 150(F

Corrosion Allowance	Zero

Tube:	(Tube sizes designated by OD dimensions)

All sizes up to 1”		ASTM A269 GR TP304 SMLS

1 1/2” and larger		ASTM A269 GRTP304 SMLS or Welded.

Tube		Minimum Wall 	Conflat					Thru

Size		Thickness	Flange			No.	B.C.		Hole

(Od):		(Inches)		Size			Bolts	Dia.		Dia.

1/4"		0.035"		1 1/3” Nom. O.D.		6	1.062”		.172”

3/8"		0.035"		1 1/3” Nom. O.D.		6	1.062”		.172”

1/2"		0.035"		1 1/3” Nom. O.D.		6	1.062		.172”

3/4"		0.035"		2 1/8” Nom.. O.D.	4	1.625”		.265”

1"		0.065"		2 3/4” Nom. O.D.		6	2.312”		.265”

1 1/2"		0.065"		2 3/4” Nom.. O.D.	6	2.312”		.265”

2”		0.065"		3 3/8” Nom. O.D.		8	2.85”		.332”

2 1/2”		0.065”		4 1/2” Nom. O.D.		8	3.628”		.332”

4”		0.083”		6” Nom. O.D.		16	5.128”		.332”

6"		0.083		8”  Nom. O.D.		20	7.128”		.332”

8”		0.120		10” Nom. O.D.		24	9.128”		.332”

10”		0.120		12” Nom. O.D.		32	11.181”		.332”

12”		0.120		14” Nom. O.D.		30	12.810”		.390”

14”		0.120		16 1/2” Nom.. O.D.	36	15.310”		.390”

T5  Cont. on next page.

T5

Flanges:	All flanges to be Conflat tube fittings 304 Stainless Steel.

Flange bolts and washers to be stainless steel, with silicon bronze nuts.

Fittings:	All fittings to be 304 butt weld or flanged O.D. tube.  Wall thickness to match the tube wall thickness.

Valves:	Valves shall be furnished under their own unique specification.

Cleaning:	Internal surfaces shall be cleaned and protected by Buyer approved procedures suitable for class 100 air service.

Notes:

1.	Tubing to be internally cleaned, dried and ends sealed during shipping, storing and installation.  Tube ID to be free of hydrocarbon contamination.

2.	Fittings to be cleaned after manufacturing and sealed in plastic bags during shipping, storing and installation.

3.	Tubing surface finish to be standard white pickled I.D. & O.D.

4.	Material manufactures certificate of compliance to applicable ASTM specifications are required and must accompany shipment.

5.	Tubing, flanges and fittings to be etched or stamped with manufacturers name, part number and material type.

6.	Conflat flanges to be made from either electro slag remelt, vacuum remelt or crossforged material.

C1

PIPING DESIGN AND MATERIAL SPECIFICATION

Service:                             Cryogenic

Design Conditions:

Pressure                           150 PSIG

Temperature                    -320(F to 350(F

Corrosion Allowance       None

Tube:

All sizes                          Type “l” Copper - Hard Drawn

ASTM B88,B280, copper tube designated by its

Nominal sizes, not  OD (UON).

Fittings:

All sizes                           Wrought copper

ASTM B75

All fittings to be female solder cup ends.

Valves:                                       Valves shall be furnished under their own unique specification.

Brazing;

All joints shall be brazed using brazing alloy bcup-5 (American Welding Society Designation). No flux is required; however a purge with argon or nitrogen is required during heating or brazing periods.