## Sheet1
This shows the mapping of a single D37 Female bulkhead mounted connector to 4 of the terminal blocks that come with the Etherstax ES2113 Acromag Binary IO boards.
12 of these connector assemblies are used in a single 384 channel Acromag Binary IO chassis. The connections are made by 24 AWG stranded wire, 12 inches long.
D37 Pin Number | Terminal Block | Pin | Function | Wire Color | The D1100251 384 channel Binary Output Chassis uses several types of components internally. Here's a list of part numbers such that the chassis can be built: 37 Pin Dsub - 6737FER-ND, Pins for Dsub - 82SECT-ND, Etherstax Module ES2113-0010, Bulkhead feedthrough RJ45 - A33706, 3A Circuit Breaker 486-2381-ND or equivalent, 3-Pin Male Conec power entry connector, LED with inline current diode or resistor. D1100252 Front Panel and D1100253 Rear Panel. White hook-up wire A2844/7W-1000-ND, Black hook-up wire CN119B-250-ND
1 | A | 1 | GND | Black
2 | A | 2 | BI 0 | White
3 | A | 3 | BI 1 | White
4 | A | 4 | BI 2 | White
5 | A | 5 | BI 3 | White
6 | A | 6 | BI 4 | White
7 | A | 7 | BI 5 | White
8 | A | 8 | BI 6 | White
9 | A | 9 | BI 7 | White
10 | B | 2 | BI 8 | White
11 | B | 3 | BI 9 | White
12 | B | 4 | BI 10 | White
13 | B | 5 | BI 11 | White
14 | B | 6 | BI 12 | White
15 | B | 7 | BI 13 | White
16 | B | 8 | BI 14 | White
17 | B | 9 | BI 15 | White
18 | No Connection
19 | No Connection
20 | C | 1 | GND | Black
21 | C | 2 | BI 16 | White
22 | C | 3 | BI 17 | White
23 | C | 4 | BI 18 | White
24 | C | 5 | BI 19 | White
25 | C | 6 | BI 20 | White
26 | C | 7 | BI 21 | White
27 | C | 8 | BI 22 | White
28 | C | 9 | BI 23 | White
29 | D | 2 | BI 24 | White
30 | D | 3 | BI 25 | White
31 | D | 4 | BI 26 | White
32 | D | 5 | BI 27 | White
33 | D | 6 | BI 28 | White
34 | D | 7 | BI 29 | White
35 | D | 8 | BI 30 | White
36 | D | 9 | BI 31 | White
37 | No Connection