## Corner Left
Remote Access Chassis Corner |  | Left Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | L | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | L | EK1101 | 0 | 0V | P | TBLOCK
24V | violet | L | EK1101 | 0 | + | P | TBLOCK
0V | gray | L | EK1101 | 0 | – | P | TBLOCK
24V | violet | L | EL9400 | 11 | 24V | P | TBLOCK
0V | gray | L | EL9400 | 11 | 0V | P | TBLOCK
24V | violet | L | EL9400 | 11 | + | P | TBLOCK
0V | gray | L | EL9400 | 11 | – | P | TBLOCK
24V | violet | L | EL6692 | 22 | 24V | P | TBLOCK
0V | gray | L | EL6692 | 22 | 0V | P | TBLOCK
Communication
EtherCAT in | CAT5 | L | EK1101 | 0 | X1 | Comm. | Front | In
EtherCAT out | CAT5 | L | EK1101 | 0 | X2 | Comm. | Front | Out
Safety
Safety sensor 1 + | brown | L | EL1904 | 3 | +I1 | BI | 8 | 1
Safety sensor 1 – | black | L | EL1904 | 3 | –I1 | BI | 8 | 20
Safety sensor 2 + | brown | L | EL1904 | 3 | +I2 | BI | 8 | 2
Safety sensor 2 – | black | L | EL1904 | 3 | –I2 | BI | 8 | 21
Safety sensor 3 + | brown | L | EL1904 | 3 | +I3 | BI | 8 | 3
Safety sensor 3 – | black | L | EL1904 | 3 | –I3 | BI | 8 | 22
Safety sensor 4 + | brown | L | EL1904 | 3 | +I4 | BI | 8 | 4
Safety sensor 4 – | black | L | EL1904 | 3 | –I4 | BI | 8 | 23
Safety relay 1 + | orange | L | EL2904 | 4 | +O1 | BO | 8 | 5
Safety relay 1 – | black | L | EL2904 | 4 | –O1 | BO | 8 | 24
Safety relay 2 + | orange | L | EL2904 | 4 | +O2 | BO | 8 | 6
Safety relay 2 – | black | L | EL2904 | 4 | –O2 | BO | 8 | 25
Safety relay 3 + | orange | L | EL2904 | 4 | +O3 | BO | 8 | 7
Safety relay 3 – | black | L | EL2904 | 4 | –O3 | BO | 8 | 26
Safety relay 4 + | orange | L | EL2904 | 4 | +O4 | BO | 8 | 8
Safety relay 4 – | black | L | EL2904 | 4 | –O4 | BO | 8 | 27
Temperature
Temperature Supply 1 + | red | L | EL3202 | 6 | +R1 | AI | 6 | 1-2
Temperature Supply 1 – | black | L | EL3102 | 6 | –R1 | AI | 6 | 1-4
Temperature Readback 1 + | green | L | EL3102 | 6 | +R1 | AI | 6 | 1-1
Temperature Readback 1 – | white | L | EL3102 | 6 | –R1 | AI | 6 | 1-3
Temperature Supply 2 + | red | L | EL3202 | 6 | +R2 | AI | 6 | 2-2
Temperature Supply 2 – | black | L | EL3102 | 6 | –R2 | AI | 6 | 2-4
Temperature Readback 2 + | green | L | EL3102 | 6 | +R2 | AI | 6 | 2-1
Temperature Readback 2 – | white | L | EL3102 | 6 | –R2 | AI | 6 | 2-3
Communication
SM fiber EX | SM fiber | L | EK1521 | 7 | X1 | Comm. | 9 | EX
SM fiber EY | SM fiber | L | EK1521 | 9 | X1 | Comm. | 9 | EY
MM fiber corner | MM fiber | L | EK1521 | 12 | X1 | Comm. | 9 | Vertex
PTP | CAT5 | L | EL6688 | 14 | X1 | Comm. | 9 | PTP
Serial
H0 weather | D-sub | L | EL6002 | 16 | X1 | Serial | 7 | 1
H0 atomic clock | D-sub | L | EL6002 | 16 | X2 | Serial | 7 | 2
H0 GPS 1 | D-sub | L | EL6002 | 18 | X1 | Serial | 7 | 3
H0 GPS 2 | D-sub | L | EL6002 | 18 | X2 | Serial | 7 | 4
H0 timing master | D-sub | L | EL6022 | 20 | X1 | Serial | 7 | 7
Spare RS422 | D-sub | L | EL6022 | 20 | X2 | Serial | 7 | 8
Communication (H1 only)
H2 input | CAT5 | L | EL6692 | 22 | X1 | Comm. | Rear port | 1
H2 output | CAT5 | L | EL6692 | 22 | X2 | Comm. | Rear port | 2
Temperature terminals are coded red and blue for the supply lines and yellow for the readback lines.

## Corner Middle
Remote Access Chassis Corner |  | Middle Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
empty

## Corner Right
Remote Access Chassis Corner |  | Right Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
empty

## End Left
Remote Access Chassis End |  | Left Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | L | EK1101 | 0 | 24V | P | TBLOCK
0V | gray | L | EK1101 | 0 | 0V | P | TBLOCK
24V | violet | L | EK1101 | 0 | + | P | TBLOCK
0V | gray | L | EK1101 | 0 | – | P | TBLOCK
Communication
EtherCAT in | CAT5 | L | EK1101 | 0 | X1 | Comm. | Front | In
EtherCAT out | CAT5 | L | EK1101 | 0 | X2 | Comm. | Right | 4-X1
Temperature
Temperature Supply 1 + | red | L | EL3202 | 2 | +R1 | AI | 6 | 1-2
Temperature Supply 1 – | black | L | EL3102 | 2 | –R1 | AI | 6 | 1-4
Temperature Readback 1 + | green | L | EL3102 | 2 | +R1 | AI | 6 | 1-1
Temperature Readback 1 – | white | L | EL3102 | 2 | –R1 | AI | 6 | 1-3
Temperature Supply 2 + | red | L | EL3202 | 2 | +R2 | AI | 6 | 2-2
Temperature Supply 2 – | black | L | EL3102 | 2 | –R2 | AI | 6 | 2-4
Temperature Readback 2 + | green | L | EL3102 | 2 | +R2 | AI | 6 | 2-1
Temperature Readback 2 – | white | L | EL3102 | 2 | –R2 | AI | 6 | 2-3
Communication
MM fiber end | MM fiber | L | EK1521 | 4 | X1 | Comm. | Rear port | 1
Temperature terminals are coded red and blue for the supply lines and yellow for the readback lines.

## End Middle
Remote Access Chassis End |  | Middle Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
empty

## End Right
Remote Access Chassis End |  | Right Rail
Name | Color | Rail | Module | Number | Channel | Type | Adapter | Pin
Power
24V | violet | R | EK1501 | 0 | 24V | P | TBLOCK
0V | gray | R | EK1501 | 0 | 0V | P | TBLOCK
24V | violet | R | EK1501 | 0 | + | P | TBLOCK
0V | gray | R | EK1501 | 0 | – | P | TBLOCK
24V | violet | R | EL6692 | 4 | 24V | P | TBLOCK
0V | gray | R | EL6692 | 4 | 0V | P | TBLOCK
Communication
Corner EtherCAT in | SM fiber | R | EK1501 | 0 | X1 | Comm. | 1 | Vertex
Corner EtherCAT out 1 | SM fiber | R | EK1501 | 0 | X2 | Comm. | 1 | Ext.
Corner EtherCAT out 2 | CAT5 | R | EK1110 | 10 | X1 | Comm. | 1 | Ext.
End EtherCAT in | CAT5 | R | EL6692 | 4 | X2 | Comm. | Left | 0-X2
End EtherCAT out | CAT5 | R | EL6692 | 4 | X2 | Comm. | Front | Out
Safety
Safety sensor 1 + | brown | R | EL1904 | 1 | +I1 | BI | 2 | 1
Safety sensor 1 – | black | R | EL1904 | 1 | –I1 | BI | 2 | 20
Safety sensor 2 + | brown | R | EL1904 | 1 | +I2 | BI | 2 | 2
Safety sensor 2 – | black | R | EL1904 | 1 | –I2 | BI | 2 | 21
Safety sensor 3 + | brown | R | EL1904 | 1 | +I3 | BI | 2 | 3
Safety sensor 3 – | black | R | EL1904 | 1 | –I3 | BI | 2 | 22
Safety sensor 4 + | brown | R | EL1904 | 1 | +I4 | BI | 2 | 4
Safety sensor 4 – | black | R | EL1904 | 1 | –I4 | BI | 2 | 23
Safety relay 1 + | orange | R | EL2904 | 2 | +O1 | BO | 2 | 5
Safety relay 1 – | black | R | EL2904 | 2 | –O1 | BO | 2 | 24
Safety relay 2 + | orange | R | EL2904 | 2 | +O2 | BO | 2 | 6
Safety relay 2 – | black | R | EL2904 | 2 | –O2 | BO | 2 | 25
Safety relay 3 + | orange | R | EL2904 | 2 | +O3 | BO | 2 | 7
Safety relay 3 – | black | R | EL2904 | 2 | –O3 | BO | 2 | 26
Safety relay 4 + | orange | R | EL2904 | 2 | +O4 | BO | 2 | 8
Safety relay 4 – | black | R | EL2904 | 2 | –O4 | BO | 2 | 27
Serial
H0 weather | D-sub | L | EL6002 | 6 | X1 | Serial | 7 | 1
H0 GPS 1 | D-sub | L | EL6002 | 6 | X2 | Serial | 7 | 2
H0 timing master | D-sub | L | EL6022 | 8 | X1 | Serial | 7 | 7
Spare RS422 | D-sub | L | EL6022 | 8 | X2 | Serial | 7 | 8