## Slide 1: BSC HEPI Motion
Tim MacDonald
9/26/14
Notes: Check Hugos log entry

## Slide 2: The Issue
Ground Motion
Acceptance Requirements
Optics Suspension
First Isolation Stage
Notes: Get better plots from laura

## Slide 3: LASTI Result (2005)
LASTI measurements suggested floor motion was coupled with pier motion
Notes: Check if amplitude is calibrated (nope)
See if amplitude is close to LHO measurements

## Slide 4: Modeling Efforts
Christophe at the University of Brussels (Abaqus)
Stanford (ANSYS)

## Slide 5: Modeling Results
Models do not clearly agree with measurements or between models
Variation of boundary conditions led to different results
Unclear which BCs to use

## Slide 6: Real Information Needed
Want specific mode shapes to determine how the floor and the rest of the structure is moving
B&K system can be used for this function
Notes: Talk about reciprocity

## Slide 7: B&K Setup at LHO
Three 4506 accelerometers
One 8340 accelerometers (the big one)
8208 Impact hammer (3 lb)
8206 Impact hammer
4506
4506
4506
8340

## Slide 8: Initial Measurements
Hammer hits on the floor and pier
Nothing seen near 8 Hz
Low coherence on 4506s
Moved 8340 to pier, still nothing

## Slide 9: Initial Measurements
Check L4C data and location
L4C location in foot had not been hit
Tried an impact on the crossbeam
Chart: 8340 Frequency Response by Impact Location
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Floor | 8.9463e-06 | 1.1213e-05 | 1.0185e-05 | 8.9741e-06 | 7.8823e-06 | 7.1713e-06 | 6.6907e-06 | 6.2701e-06 | 5.5769e-06 | 5.2211e-06 | 4.8145e-06 | 4.008e-06 | 3.4224e-06 | 2.9767e-06 | 1.7188e-06 | 1.9841e-06 | 3.2958e-06 | 4.501e-06 | 6.3646e-06 | 1.0848e-05 | 1.9618e-05 | 4.6758e-05 | 2.7529e-05 | 1.6619e-05 | 1.1377e-05 | 8.3012e-06
Crossbeam | 0.00011261 | 9.0784e-05 | 4.2489e-05 | 4.682e-05 | 4.9565e-05 | 7.2581e-05 | 0.00010281 | 0.00017716 | 0.00028258 | 0.00024902 | 0.00016215 | 0.00016526 | 0.00024168 | 0.00047372 | 0.00067615 | 0.00056396 | 0.00045125 | 0.00038084 | 0.00033589 | 0.00030278 | 0.00025193 | 0.00023796 | 0.00034444 | 0.00029485 | 0.0002646 | 0.0002437
Pier Base | 0.0010393 | 0.0010932 | 0.00085576 | 0.00071336 | 0.00061895 | 0.0005519 | 0.00050048 | 0.00045334 | 0.0004137 | 0.00036395 | 0.00031716 | 0.00028935 | 0.00028338 | 0.00030607 | 0.00031509 | 0.00029908 | 0.00033411 | 0.00041008 | 0.00053551 | 0.00078271 | 0.0014069 | 0.0028211 | 0.0012305 | 0.00071312 | 0.00051348 | 0.00041439
Pier Top | 0.00014062 | 0.00023961 | 0.00021324 | 0.00015325 | 0.00011839 | 0.00012371 | 0.0001726 | 0.0002683 | 0.00038433 | 0.00038797 | 0.0004165 | 0.00049143 | 0.00060975 | 0.00078138 | 0.0008132 | 0.00082877 | 0.0011261 | 0.0016356 | 0.0024661 | 0.0040674 | 0.0081633 | 0.012137 | 0.0052812 | 0.0032846 | 0.0024196 | 0.0019406
Floor | 8.9463e-06 | 1.1213e-05 | 1.0185e-05 | 8.9741e-06 | 7.8823e-06 | 7.1713e-06 | 6.6907e-06 | 6.2701e-06 | 5.5769e-06 | 5.2211e-06 | 4.8145e-06 | 4.008e-06 | 3.4224e-06 | 2.9767e-06 | 1.7188e-06 | 1.9841e-06 | 3.2958e-06 | 4.501e-06 | 6.3646e-06 | 1.0848e-05 | 1.9618e-05 | 4.6758e-05 | 2.7529e-05 | 1.6619e-05 | 1.1377e-05 | 8.3012e-06
Crossbeam | 0.00011261 | 9.0784e-05 | 4.2489e-05 | 4.682e-05 | 4.9565e-05 | 7.2581e-05 | 0.00010281 | 0.00017716 | 0.00028258 | 0.00024902 | 0.00016215 | 0.00016526 | 0.00024168 | 0.00047372 | 0.00067615 | 0.00056396 | 0.00045125 | 0.00038084 | 0.00033589 | 0.00030278 | 0.00025193 | 0.00023796 | 0.00034444 | 0.00029485 | 0.0002646 | 0.0002437
Pier Base | 0.0010393 | 0.0010932 | 0.00085576 | 0.00071336 | 0.00061895 | 0.0005519 | 0.00050048 | 0.00045334 | 0.0004137 | 0.00036395 | 0.00031716 | 0.00028935 | 0.00028338 | 0.00030607 | 0.00031509 | 0.00029908 | 0.00033411 | 0.00041008 | 0.00053551 | 0.00078271 | 0.0014069 | 0.0028211 | 0.0012305 | 0.00071312 | 0.00051348 | 0.00041439
Pier Top | 0.00014062 | 0.00023961 | 0.00021324 | 0.00015325 | 0.00011839 | 0.00012371 | 0.0001726 | 0.0002683 | 0.00038433 | 0.00038797 | 0.0004165 | 0.00049143 | 0.00060975 | 0.00078138 | 0.0008132 | 0.00082877 | 0.0011261 | 0.0016356 | 0.0024661 | 0.0040674 | 0.0081633 | 0.012137 | 0.0052812 | 0.0032846 | 0.0024196 | 0.0019406
Chart: 8340 Coherence by Impact Location
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Floor | 0.98533 | 0.97904 | 0.97989 | 0.98014 | 0.97849 | 0.97472 | 0.9688 | 0.96336 | 0.96212 | 0.97976 | 0.97468 | 0.95024 | 0.97717 | 0.90383 | 0.84181 | 0.87958 | 0.93755 | 0.95303 | 0.96651 | 0.99116 | 0.9894 | 0.99292 | 0.99204 | 0.99681 | 0.99661 | 0.99497
Crossbeam | 0.99297 | 0.9871 | 0.95517 | 0.97919 | 0.99226 | 0.99771 | 0.99853 | 0.99909 | 0.99932 | 0.99916 | 0.99924 | 0.99912 | 0.99911 | 0.99944 | 0.99952 | 0.99958 | 0.99959 | 0.99958 | 0.999 | 0.99918 | 0.99797 | 0.9959 | 0.99945 | 0.99938 | 0.9993 | 0.99911
Pier Base | 0.82274 | 0.83622 | 0.86235 | 0.87597 | 0.88245 | 0.88845 | 0.89609 | 0.90515 | 0.9162 | 0.92277 | 0.92593 | 0.93454 | 0.94537 | 0.96189 | 0.97097 | 0.97081 | 0.97981 | 0.98668 | 0.99164 | 0.99589 | 0.99775 | 0.99917 | 0.99802 | 0.99572 | 0.9926 | 0.9911
Pier Top | 0.92372 | 0.95533 | 0.95328 | 0.93958 | 0.94287 | 0.97455 | 0.99242 | 0.99699 | 0.99806 | 0.99726 | 0.99704 | 0.99714 | 0.99766 | 0.99849 | 0.99857 | 0.99838 | 0.99855 | 0.99846 | 0.99811 | 0.99751 | 0.99636 | 0.99736 | 0.99892 | 0.99878 | 0.9987 | 0.99862
8340 Location
LHO X
LHO Y

## Slide 10: Full Floor System Measurement
Created hit pattern up and around BSC
Included the crossbeam

## Slide 11: Full System Results
Motion in crossbeam roughly 2-3x pier motion
Almost no motion visible in the floor
Crossbeam does not appear to bend
Lack of impact at these points creates illusion of bending. Motion only appears at impact points.
Notes: Check amplitude of floor motion

## Slide 12: Measurements including HEPI
New sequence including the HEPI actuator system
Large motion seen with the foot, about twice the crossbeam
Odd in that it only appears at the low point of the foot
Notes: Talk about why the difference matters

## Slide 13: New Modeling at Stanford
Now that we believe the HEPI system is the source of the issue, see if we can properly model it
Initial modeling did not include the pier or actuators
Odd motion not visible, frequency of 4 Hz

## Slide 14: Actuator Addition
Added actuators based on Brian’s old model at 8 Hz
Frequency more reasonable, still nothing on the foot motion
Desired K | 1.6e7 N/m
E | 1.88e11 Pa
Length | 0.25 m
Radius | 0.0026 m
New Freq | 14.68 Hz
See https://alog.ligo-la.caltech.edu/SEI/index.php?callRep=543
Notes: Point to log entry

## Slide 15: Piers and Full Model Setup
Added piers, attached end of actuators to pier with stiff structures
Fixed supports at floor
Component | Mass | Material
Piers | 750 kg each | Steel
HEPI Housing | 160 each | Steel
HEPI Foot | 20 kg each | Steel
Crossbeam | 480 kg each | Steel
Support Tube Attach | 140 kg each | Steel
Support Tubes | 460 kg each | Steel
Stage 0 | 700 kg | Aluminum
Total Mass w/o Piers/Housing | 3220 kg | -
Total Mass | 7060 kg | -

## Slide 16: Full Model Results
Beam tube direction mode at 11.4 Hz

## Slide 17: Other Attempts
Static structural testing at crossbeam and foot
Response spectra at crossbeam and foot
No new insight

## Slide 18: Stiffness Data from Measurements
Chart: Frequency (Hz)
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Pier | 164760.3329 | 740529.0932 | 2318463.641 | 5335293.3223 | 7977952.7275 | 8234279.0329 | 7210047.7773 | 6574028.2325 | 8242346.4911 | 9478682.8244 | 9720409.2751 | 9323334.7585 | 8538501.3961 | 9515255.0735 | 10717859.1685 | 8974550.8764 | 6975450.2638 | 5186656.6986 | 3503898.1994 | 1934438.0071
Crossbeam | 2338.672 | 12470.7859 | 38535.3614 | 76123.3721 | 84502.5686 | 85573.371 | 82315.6343 | 78302.5243 | 123582.7229 | 273235.6722 | 499248.336 | 617240.2435 | 484394.2119 | 537501.8814 | 972957.7219 | 1816600.2528 | 2293576.926 | 2205144.8456 | 2118291.9193 | 2113350.274
Foot | 106.2128 | 787.4939 | 2954.2648 | 8213.894 | 17627.5388 | 24822.345 | 26315.3577 | 26983.1882 | 35460.6664 | 64998.2782 | 95885.5757 | 134546.2564 | 193399.778 | 262454.2823 | 362584.5237 | 511888.4363 | 685992.9186 | 768829.9828 | 872338.429 | 1028148.8933
Coherence above 0.9
Notes: Get stiffness at accel location for both 8340 locations

## Slide 19: Proposed Solutions
Add another actuator
  Likely not possible due to space and construction issues
See if the mode can be controlled with existing actuators
Replace/modify the crossbeam
Add vibration absorbers to crossbeam
Stiffen the piers
Reaction mass actuator
Notes: Adding HEPI actuator
-impractical because we don’t have more and there’s no space
Modifying crossbeam useful if foot moving more or allows control
Stiffening the piers useful if it allows control with existing actuators, could move some frequencies apart

## Slide 20: Next Steps
Get foot measurement resolved
  Will determine usefulness of crossbeam modification
Paper study of controller for 8 Hz mode
  Can it be controlled with existing system?
Create models of passive and active damping systems
  Determine feasibility
Create model with additional actuator
  Probably not practical
Create model with stiffer piers
  Could make HEPI control simpler
Notes: Remember to ask fabrice to do this

## Slide 21: Extra Slides

## Slide 22
/SeismicSVN/seismic/HEPI/Stanford/Transfer/2014_09_25_H1_ETMY_HEPI_Controller/

## Slide 23
SeiSVN/seismic/Common/Documents/2014_09_04_HEPI_TMDs/